## gen
Bus # | 1 | 2 | 3
Gen id | 1' | 1' | 1'
type | GENROU | GENROU | GENROU
T'd0 | 6 | 6 | 6
T''d0 | 0.5 | 0.5 | 0.5
T'q0 | 1 | 1 | 1
T''q0 | 0.05 | 0.05 | 0.05
H | 15.76 | 2.56 | 3.01
D | 0 | 0 | 0
Xd | 1.4 | 1.4 | 1.4
Xq | 1.35 | 1.35 | 1.35
X'd | 0.3 | 0.3 | 0.3
X'q | 0.6 | 0.6 | 0.6
X''d=X''q | 0.2 | 0.2 | 0.2
Xl | 0.1 | 0.1 | 0.1
S(1.0) | 0 | 0 | 0
S(1.2) | 0 | 0 | 0
Ra | 0.005 | 0.005 | 0.005

## exc
Bus # | 1 | 2 | 3
Gen id | 1' | 1' | 1'
type | SEXS | SEXS | SEXS
TA_o_TB | 0 | 0 | 0
TB | 10 | 10 | 10
K | 10 | 10 | 10
TE | 0.1 | 0.1 | 0.1
Emin | 0 | 0 | 0
Emax | 3 | 3 | 3

## gov
Bus # | 1 | 2 | 3
Gen id | 1' | 1' | 1'
type | GAST | GAST | GAST
R | 0.08 | 0.08 | 0.08
T1 | 0.5 | 0.5 | 0.5
T2 | 0.5 | 0.5 | 0.5
T3 | 3 | 3 | 3
Ambient temperature load limit | 1 | 1 | 1
KT | 2 | 2 | 2
VMAX | 1 | 1 | 1
VMIN | 0 | 0 | 0
Dturb | 0 | 0 | 0

## pss
Bus # | 1 | 2 | 3
Gen id | 1' | 1' | 1'
type | IEEEST | IEEEST | IEEEST
A1 | 1.013 | 1.013 | 1.013
A2 | 0.013 | 0.013 | 0.013
A3 | 0 | 0 | 0
A4 | 0 | 0 | 0
A5 | 1.013 | 1.013 | 1.013
A6 | 0.113 | 0.113 | 0.113
T1 | 3 | 3 | 3
T2 | 0.02 | 0.02 | 0.02
T3 | 0 | 0 | 0
T4 | 0 | 0 | 0
T5 | 1.65 | 1.65 | 1.65
T6 | 1.65 | 1.65 | 1.65
KS | 3 | 3 | 3
LSMAX | 0.1 | 0.1 | 0.1
LSMIN | -0.1 | -0.1 | -0.1
VCU | 0 | 0 | 0
VCL | 0 | 0 | 0

## regca
Bus
ID
LVPL switch, 0: LVPL not present, 1: LVPL present
Tg, Converter time constant, second
Rrpwr, LVPL ramp rate limit (pu/s)
Brkpt, LVPL voltage 2 (pu)
Zerox, LVPL voltage 1 (pu)
Lvpl1, LVPL gail (pu)
Volim, Voltage limit for High Voltage Reactive Current Management, pu
Lvpnt1, High Voltage point for Low Voltage Active Current Management, pu
Lvpnt0, High Voltage point for Low Voltage Active Current Management, pu
Iolim, Current limit for HVRCM, pu (< 0)
Tfltr, Voltage filter time constant for LVRCM (s)
Khv, Overvoltage compensation gain used in HVRCM (>=0 and < 1)
Iqrmax, Upper limit on Rate of change for reactive curent (pu/s)
Iqrmin, Lower limit on Rate of change for reactive curent (pu/s)
Accel, Acc. factor for smoothing out voltage & angle calculations (>0 and <=1)
fbase
mvabase

## reecb
Bus
ID
PFFLAG (Power factor flag): 1 - power factor control; 0: Q control
VFLAG: 1 if Q control; 0 voltage control
QFLAG: 1 if voltage/Q control; 0 if pf/Q control
PQFLAG: 1 for P priority, 0 for Q priority
Vdip (pu), low voltage threshold for reactive current injection
Vup (pu), high voltage threshold for reactive current injection
Trv (s), Voltage filter time constant
dbd1 (pu), Voltage error dead band lower threshold (<=0)
dbd2 (pu), Voltage error dead band upper threshold (>=0)
Kqv (pu), Reactive current injection gain
Iqhl (pu), Upper limit on reactive current injection Iqinj
Iqll (pu), Lower limit on reactive current injection Iqinj
Vref0 (pu), User defined reference (if 0, initialized by model)
Tp (s), Filter time constant for electrical power
QMax (pu), limit for reactive power regulator
QMin (pu) limit for reactive power regulator
VMAX (pu), Max. limit for voltage control
VMIN (pu), Min. limit for voltage control
Kqp (pu), Reactive power regulator proportional gain
Kqi (pu), Reactive power regulator integral gain
Kvp (pu), Voltage regulator proportional gain
Kvi (pu), Voltage regulator integral gain
Tiq (s), Time constant on delay s4
dPmax (pu/s) (>0) Power reference max. ramprate
dPmin (pu/s) (<0) Power reference min. ramprate
PMAX (pu), Max. power limit
PMIN (pu), Min. power limit
Imax (pu), Maximum allowable total converter current limit
Tpord (s), Power filter time constant

## repca
Bus
ID
Remote bus number or 0 for local voltage control
Monitored branch FROM bus
Monitored branch TO bus
Monitored branch ID (enter within single quotes)
VCFlag, droop flag (0: with droop,1: line drop compensation)
RefFlag, flag for V or Q control(0: Q control, 1: V control)
Fflag, 0: disable frequency control, 1: enable
Tfltr, Voltage or reactive power measurement filter time constant (s)
Kp, Reactive power PI control proportional gain (pu)
Ki, Reactive power PI control integral gain (pu)
Tft, Lead time constant (s)
Tfv, Lag time constant (s)
Vfrz, Voltage below which State s2 is frozen (pu)
Rc, Line drop compensation resistance (pu)
Xc, Line drop compensation reactance (pu)
Kc, Reactive current compensation gain (pu)
emax, upper limit on deadband output (pu)
emin, lower limit on deadband output (pu)
dbd1, lower threshold for reactive power control deadband (<=0)
dbd2, upper threshold for reactive power control deadband (>=0)
Qmax, Upper limit on output of V/Q control (pu)
Qmin, Lower limit on output of V/Q control (pu)
Kpg, Proportional gain for power control (pu)
Kig, Proportional gain for power control (pu)
Tp, Real power measurement filter time constant (s)
fdbd1, Deadband for frequency control, lower threshold (<=0)
fdbd2, Deadband for frequency control, upper threshold (>=0)
femax, frequency error upper limit (pu)
femin, frequency error lower limit (pu)
Pmax, upper limit on power reference (pu)
Pmin, lower limit on power reference (pu)
Tg, Power Controller lag time constant (s)
Ddn, droop for over-frequency conditions (pu)
Dup, droop for under-frequency conditions (pu)

## pll
Bus | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
ke | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
te | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05

## vm
Bus | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
te | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02

## gen_para
GENROU
T'd0
T''d0
T'q0
T''q0
H
D
Xd
Xq
X'd
X'q
X''d=X''q
Xl
S(1.0)
S(1.2)
Ra

## exc_para
SEXS
TA_o_TB
TB
K
TE
Emin
Emax

## gov_para
TGOV1 | HYGOV | GAST
R | R, Permanent Droop | R(Speed Droop)
T1(>0)(sec) | r, Temporary Droop | T1(>0)
V MAX | Tr(>0) Governor Time Constant | T2(>0)
V MIN | Tf(>0) Filter Time Constant | T3(>0)
T2(sec) | Tg(>0) Servo Time Constant | Ambient Temperature Load Limit
T3(>0)(sec) | VELM, Gate Velocity Limit | KT
Dt | GMAX, Maximum Gate Limit | VMAX
| GMIN, Minimum Gate Limit | VMIN
| TW(>0) Water Time Constant | Dturb
At, Turbine Gain
Dturb, Turbine Damping
aNL, No Load Flow

## pss_para
IEEEST
A1
A2
A3
A4
A5
A6
T1
T2
T3
T4
T5
T6
KS
LSMAX
LSMIN
VCU
VCL